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APCOCHAR –WB-100
Intumescent Coating


Product Description
A water borne intumescent coating for the fire protection of interior I section structural steelwork.

Designed Use
• Provides 30, 60 and 90 minutes fire resistance to structural steel.
• Tested in accordance with BS476; Part 21: 1987 by Warrington Fire Research and Building Research Establishment.
• Highly competitive loadings for most steel section sizes giving reduced application costs.
• Easy application properties.
• Topcoats are not required in C1 interior environments. When using topcoats please ensure to check compatibility with Berger Paints manufacturer before application.
• Recommended for on-site application. Off-site applications must be topcoated before being taken outside and carefully handled (See application notes)
• Recommended for interior environments classified as C1,C2, C3 under the definitions in ISO 12944 – 2:1998 with suitable topcoats.

	





 Physical Data
	Volume Solids
(Based on ASTM D2697)
	70%+ 2%

	
	Typical Dry Film Thickness
	200 - 1600 microns

	
	Wet Film Thickness
	285-2285 microns

	
	Theoretical Coverage
	 1.87 m2 /litre @ 375 microns DFT

	
	
VOC “As Supplied” (Based on ASTM D3960)
	Minimal VOCs – EPA Compliant

	
	Colour
	Off White

	
	Finish
	Matt



	

 Application Details
	Method Of Application

	
	
 Airless Spray, Brush, Roller
	
At 375 microns dft and RH 70%
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	Drying Time

	
Surface Temperature
	
Dust Free
	
Hard Dry
	Over coating Interval

	
	
	
	Minimum
	Maximum

	20°C
	1 hour
	4 hours
	4 hours
	See Below*

	30°C
	40 mins
	70 mins
	70 mins
	See Below*

	40°C
	½ hour
	50 mins
	50 mins
	See Below*



* Overcoating: Only overcoat with self or approved topcoat – consult Berger Paints for advice. Maximum overcoating time is indefinite providing the surface is clean and the coating is sound. Coated surfaces must be kept in controlled, dry conditions until top coated or degradation may occur.

	Airless spray @750 microns dft (and RH 70%)

	
Surface Temperature
	
Dust Free
	
Hard Dry (Over coating)

	20°C
	2 hours
	12 hours

	30°C
	1½ hours
	4 hours

	40°C
	1 hour
	3 hours



	


Additional Information
	Thinner
	Fresh Water

	
	Storage Instruction
	Store in dry, cool and shaded area.

	
	Flash Point
	Above 55°C

	
	Packaging
	20 litres

	
	Shelf Life @ 23°C
	6 months in closed containers



Surface Preparation
Degrease where necessary to SSPC-SP1 solvent cleaning to remove traces of oil, grease and other contamination prior to blasting. All sharp edges should be ground and weld spatter removed. Blast clean to Swedish Standard SIS 05 5900 Sa 2.5 and maximum profile of 75 microns. Apply one coat Epilux 78, Epilux 76, Epilux 74, Rapid Air Dry 10 primers to a dft of 50-75 microns dft. Kindly contact Berger Paints for any other compatible primer and topcoats.

	


Application Notes
	Method
	Airless Spray
	Roller
	Brush
	Conventional
Spray
	Aut omatic 
Spray

	
	
Output fluid pressure tip size
	Min  3000  psi
21-25 thou
	Yes
	Yes
	No
	No
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Mix the paint thoroughly before use. 
Brush/roller application will typically give up to 500 microns dft for multi-coat application, but up to 1mm can be achieved.

Highest standard of decorative finish is only likely to be achieved with careful airless spray application.
Off-site applications must be allowed sufficient hardening time before moving. Coated sections should be packed and handled so as to minimize damage to coating and prevent ponding by water and should be stored and transported under cover. If possible, handling cleats should be attached to the steelwork to minimize lifting damage. Topcoat must be applied before leaving the shop. On site, all damage should be repaired to original specification.

Only apply in conditions of good ventilation which should be maintained during drying. Do not apply when rain, mist, sleet or snow are imminent. Do not apply or allow to dry below 5°C, temperatures above 10°C are preferred. During  application and drying time of paint coating, the surface should be dry and the relative humidity should not exceed 90%; the RH should be maintained as low as possible. The steel temperature should remain at least 3°C above dew point.

Safety Precautions
• Avoid contact with the skin and eyes. Wear suitable protective clothing such as overalls, goggles, dust masks and gloves. Use a barrier cream.
• Ensure that there is adequate ventilation in the area where the product is being applied. Do not breathe vapour or spray.
• This product is flammable. Keep away from sources of ignition. Do not smoke. Take precautionary measures against static discharge. In case of fire blanket flames with foam, carbon dioxide or dry chemicals.
• Refer to MSDS for further information.

First Aid
• Eyes: In the event of accidental splashes, flush eyes with water immediately and obtain medical advice.
• Skin: Wash skin thoroughly with soap and water or approved industrial cleaner.
• Do not use solvent or thinners.
• Inhalation: Remove to fresh air, loosen collar and keep patient rested.
• Ingestion: In case of accidental ingestion, do not induce vomiting. Obtain immediate medical attention.

Disclaimer
The information provided on this data sheet is not intended to be complete and is provided as general advice only. It is the responsibility of the user to ensure that the product is suitable for the purpose for which he wishes to use it. As we have no control over the treatment of the product, the standard of surface preparation of the substrate, or other factors affecting the use of this product, we are not responsible for its performance nor would we accept any liability whatsoever or howsoever arising from the use of this product unless specifically agreed to in writing by us. The information contained in this data sheet may be modified by us from time to time, and without notice, in the light of our experience and continuous product development.
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